## Slide 1
Control Systems
Stage 4: Electrical, Electronic and Communications Engineering
Dr Paul Curran
Room 145, Engineering.
paul.curran@ucd.ie
+353-1-7161846

## Slide 2: Overview of Topics
Mathematical background and problem statement.
Dominant pole placement via root locus.
Basic loop shaping.
Linear state feedback and observers.
Digital control.

## Slide 3
Section 3 - Outline
PID Controllers.
Root Locus.
Design.
Section: 3
PID

## Slide 4
PID Controllers
Section: 3
PID
PID controllers comprise the first good idea for controlling systems. Minorsky is generally credited as having played a major role both in their formulation and in their widespread adoption. It is only slightly controversial to declare that they remain the preferred method of control to this day.

## Slide 5
Performance Specification
Section: 3
PID
Recall that a great deal of the specification of control system performance is concerned with the step response of the closed-loop system. Recall also that this response will very commonly take, at least approximately, one of two distinct forms:
underdamped
overdamped

## Slide 6: Note
We have called these forms second order and first order, but they are also called underdamped and overdamped. The second order response passes over from one form to the other as the damping ratio passes through unity as it is clear from the formula for the poles that they cease being complex as the damping ratio passes through unity.
Section: 3
PID

## Slide 7: Step Response Characteristics
PID
Section: 3
Characterisation of step response asks: (i) where does the output settle? (ii) how long does it take to settle? and (iii) by how much does it overshoot? The quantifiable answers to these questions are:
(i) For constant input, the output of a stable system settles to the DC gain times the input. Partial alternative: if the steady-state error is zero then the output settles to a value equal to the input.
(ii) The 10% to 90% rise time tr (time for output to rise from 10% to 90% of the steady state value) and the 2% settling time ts(2%) (time at which output settles into (i.e. never again leaves) the 2% band around the steady state value) both measure the transient time.
(iii) The percentage overshoot PO% measures the overshoot.

## Slide 8
Three Term Controller
Section: 3
PID

## Slide 9: Note
As a matter of terminology we should note that the term “compensator” is sometimes used synonymously with “controller”. There seems to be no consensus as to whether the terms are, in fact, synonymous. Usage seems to indicate that the former is some kind of unspecified subset of the latter.
Assume ideal sensor Gsens = 1 (or alternatively absorb non-ideal sensor TF into plant model).
Section: 3
PID

## Slide 10: Note
kp = Proportional gain
ki = Integral gain
kd = Derivative gain
The time-domain expression for the controller action clearly explains the terminology. This signal becomes the input to the plant and yields the output of the plant y. This output y is fed back through the ideal (unity gain across all frequencies) sensor.
Note use of unconventional notation up to avoid confusion with unit step.
Section: 3
PID

## Slide 11
Three Term Controller
Section: 3
PID
A PID controller with all three terms introduces a gain term, a pole at 0 and two zeros.

## Slide 12
Three Term Controller
Section: 3
PID
A PI controller with both terms introduces a gain term, a pole at 0 and one zero.

## Slide 13
Three Term Controller
Section: 3
PID
A PD controller with both terms introduces a gain term and one zero.
A P controller introduces a gain term only.
I, D or ID controllers are virtually never used.

## Slide 14
Section: 3
The transfer function of a pure differentiator is s. Its frequency
response is therefore jw yielding a very high gain at very high
frequencies. Practical systems cannot respond at all (let alone
with very high gain) to very high frequencies. Even if we could
build a pure differentiator, noise (which will generally include
very high frequency components) will be greatly amplified.
In practice we try to build a system with the following transfer function:
PID
Three Term Controller

## Slide 15: Note
It should be noted that the argument also casts doubt on the prospect of building a proportional controller, doubts which control theory has a tendency to ignore since there is some sense in which we can build an acceptable approximation of a proportional controller. The “sense” is to recognise that we are building systems. I need therefore only build a system which reacts correctly (like a pure gain for example) when presented with the signals which it will see. It does not matter how it reacts to signals which it will never see. In practice all of the signals present will be band-limited, i.e. they will have a maximum frequency component. A would-be proportional controller only has to give the right gain up to this maximum.
Section: 3
PID

## Slide 16: Note
The ideal differentiator is more problematic however. It gives increasing gain with increasing frequency. A time-domain view also explains the difficulty. Noise will jump around a lot. It therefore has rather sharp edges and when I differentiate this means that the derivative will regularly jump to rather large values. Now I have repeatedly stated that linear systems do not exist. Things only look linear close to operating points. These large values that the output of the differentiator is jumping to pull the system away from the operating point to where non-linearity lurks. The most common non-linear phenomenon is saturation, where a signal reaches a maximum allowed value and is cut off. The differentiation operation tends to evoke this phenomenon.
Section: 3
PID

## Slide 17: Note
For these reasons we generally take the view that perfect differentiators cannot be realised. Instead the gain of the “differentiator” is limited. We realise the approximate differentiator:
Section: 3
PID
The idea here is that for s = jw with w reasonably small this transfer function (or rather its frequency response) will be almost the same as that of a perfect differentiator. However at higher frequencies the gain does not increased without bound but rather operates under a ceiling of kd/Td .

## Slide 18
Example 3.1
Section: 3
PID
m = 1kg
b = 10 Nsec/m
k = 20 N/m

## Slide 19: Note
The goal is to illustrate how each of the gains kp, ki and kd contributes towards obtaining:
Fast transient
Minimum overshoot
Zero steady-state error
Strictly the term should be “short” or “small” “transient” but the word “fast” is unequivocal and more descriptive.
Section: 3
PID

## Slide 20
>> Gp = tf([1],[1 10 20])
>> pole(Gp)
>> step(Gp)
Section: 3
Code
PID
The poles are at -7.2361 and -2.7639. Clearly the latter is dominant. The system should act as a first order system with a single pole at -2.7639. The corresponding time constant is 1/2.7639 = 0.3618. Five time constants is 1.8 sec approximately. So I anticipate that the transient part of the step response will be of about 1.8 sec duration. The DC gain is G(0) = 1/20 so the steady-state output for a unit step input should be 0.05.

## Slide 21
Example 3.1: Open loop response
Section: 3
PID
0.05 is indeed the final value for a unit step input. This corresponds to a large steady-state error of 0.95. The transient duration is indeed about 1.8 sec. The 10% to 90% rise time = 0.88 sec and the 2% settling time = 1.59 sec.

## Slide 22: Note
One should always check the response of the system without control. After all, if miraculously it happens to meet the specification then we do not have to do anything. More commonly it gives a sense of whether the specifications are reasonable. If the rise time of the open loop system is 10 min for example then it is almost certainly unrealistic to expect to be able to achieve a closed-loop rise time of 1 msec.
In this case we seek a controller that will reduce the rise time, reduce the settling time and eliminate the steady-state error.
Section: 3
PID

## Slide 23
Example 3.1: Proportional Controller
Section: 3
PID
The open-loop transfer function of the above system with
a proportional controller is:
Let proportional gain kp = 300. The purpose in choosing such a large gain is to ensure a closed-loop DC gain which at 300/320 is much closer to unity.
The closed-loop transfer function becomes:

## Slide 24
>> Gc = tf([300],[1])
>> G0 = series(Gp,Gc)
>> Gideal = tf([1],[1]) ideal unity feedback
>> Gcl = feedback(G0,Gideal)
>> pole(Gcl)
>> step(Gcl)
Section: 3
Code
PID
The poles are at -5 +/- 17.1756j. Clearly we have a dominant pair. The system should act as a second order system. The poles have real part -5 so the 2% settling time should be about 4/5 = 0.8 sec. The DC gain is Gcl(0) = 300/320 so the steady-state output for a unit step input should be 0.9375 which is much closer to unity.

## Slide 25
Section: 3
Code
PID
As the poles are at -5 +/- 17.1756j we have that they are the roots of the polynomial:
Comparing with:
A damping ratio of about 0.28 is not very high so the overshoot will be significant. Recall
This formula gives an expected overshoot of about 40%

## Slide 26
Example 3.1: Proportional Controller
Section: 3
PID
The closed-loop transfer function is:
The 2% settling time is 0.772 sec. The response looks like a second order response (we see overshoot and ringing). The steady-state response is 0.938. The overshoot is 39.9%

## Slide 27
Example 3.1: Proportional Derivative Controller
Section: 3
PID
The open-loop transfer function of the above system with
a PD controller is:
Let proportional gain kp = 300 and the derivative gain kd = 10. The large proportional gain again gives a closed-loop DC gain of 300/320 which is close to unity.
The closed-loop transfer function becomes:

## Slide 28
>> Gc = tf([10 300],[1])
>> G0 = series(Gp,Gc)
>> Gideal = tf([1],[1]) ideal unity feedback
>> Gcl = feedback(G0,Gideal)
>> pole(Gcl)
>> step(Gcl)
Section: 3
Code
PID
The poles are at -10 +/- 14.8324j. Clearly we have a dominant pair. The system should act as a second order system. The poles have real part -10 so the 2% settling time should be about 4/10 = 0.4 sec. The DC gain is Gcl(0) = 300/320 so the steady-state output for a unit step input should be 0.9375 as before which is much closer to unity.

## Slide 29
Example 3.1: Proportional Derivative Controller
Section: 3
PID
In this case the closed-loop poles are the roots of the closed-loop characteristic polynomial which is
As the natural frequency is unchanged whereas the damping ratio has doubled from the previous case the percentage overshoot should be reduced to about 12% and the system should be faster (actually twice as fast).
Comparing with:

## Slide 30
Example 3.1: Proportional Derivative Controller
Section: 4
PID
As the closed-loop DC gain remains 300/320 the steady-state response to a unit step input remains 0.938. The 2% settling time is 0.29 sec and PO = 15.3%.

## Slide 31
Section: 3
The problem with zeros
PID
So based on the dominant pole positions we predicted a 2% settling time of 0.4 sec and a percentage overshoot of 12% We see however a 2% settling time of 0.29 sec (so the system has become even faster than we had hoped) but a percentage overshoot of over 15% (so the overshoot has been reduced but not by as much as we expected). Apparently there is something wrong with our predictions. Although the closed-loop system has a dominant pair it is not acting like the corresponding second order system. Granted it is behaving in a manner which is somewhat similar to that predicted, but the discrepancies are hardly negligible.

## Slide 32
Section: 3
The problem with zeros
PID
The cause of the discrepancy it turns out is that the approximate equations which we have for 2% settling time and percentage overshoot in the event of there being a dominant pair assumed that the system behaved like the canonical second order system:
This system has no zero. On the other hand the actual closed-loop system which we achieve when we employ a PD controller has a zero at s = -30.

## Slide 33
Section: 3
The problem with zeros
PID
The reason why we generally ignore the zeros is because the rules which govern how they affect the settling time and overshoot are really rather fussy and depend too much upon the detailed description of the transfer function and therefore too much upon the model. Always bear in mind that this is only a model, it is not the system. Design decisions based upon the minutiae of the model will yield poor designs in practice because the actual system will differ. We must also be aware that rules which are exact are all very well, but if they are very fussy and complicated then we will not be able to employ them in design. It is my opinion that all effective design rules are simple and their simplicity is far more important than their accuracy.

## Slide 34
Section: 3
The problem with zeros
PID
Zeros can also affect dominance as the following example illustrates. Consider the system having no zeros and a dominant real pole at -1:
The unit step response of this system is determined thus:

## Slide 35
Section: 3
The problem with zeros
PID
If we consider the two transient terms in this response and ask when has the dominated term become (in magnitude) less than 1% of the dominant term we find that this occurs for
So it does not take long for the dominant term to dominate. The step response will, within a rather small fraction of a second look very much like a first order response characterised by the dominant pole.

## Slide 36
Section: 3
The problem with zeros
PID
Consider instead the system having a zero (at s = -1.1), but having the same poles including the dominant real pole at -1:
The unit step response of this system is determined thus:

## Slide 37
Section: 3
The problem with zeros
PID
The zero has caused the coefficient of the dominated pole in the partial fraction expansion (and therefore in the unit step response) to become larger in magnitude than that of the dominant pole. If we consider the two transient terms in this response again and ask when has the dominated term become (in magnitude) less than 1% of the dominant term we find that this now occurs for

## Slide 38
Section: 3
The problem with zeros
PID
So it takes longer for the dominant pole to actually dominate. For an appreciable amount of time in the early phase the step response of this system will not look like a first order response characterised by the dominant pole. Indeed the 2% settling time, were it characterised by a dominant pole at -1 should be 4/1 = 4 sec. The achieved settling time is actually less than this being about 1.74 sec (because the zero has caused the coefficient of the dominant pole term to be small). The zero has adversely affected dominance and in spite of this has actually made the response faster. It is because zeros can often have the opposite effect to what we might expect that the rules indicating how they affect response are complicated.

## Slide 39
Example 3.1: Proportional Integral Controller
Section: 3
PID
The open-loop transfer function of the above system with
a PI controller is:
Let proportional gain kp = 30 and the integral gain ki = 70. The presence of the integrator ensures a closed-loop DC gain of unity.
The closed-loop transfer function becomes:

## Slide 40
>> Gc = tf([30 70],[1 0])
>> G0 = series(Gp,Gc)
>> Gideal = tf([1],[1]) ideal unity feedback
>> Gcl = feedback(G0,Gideal)
>> pole(Gcl)
>> step(Gcl)
Section: 3
Code
PID
The poles are at -3.9538 +/- 4.2216j and -2.0924. There is a dominant real pole at -2.0924 but it is not very dominant. The imaginary parts of the dominated pair are comparable actually a bit bigger in magnitude than the real part, so again this mitigates against dominance. Of course there is also a closed-loop zero at -2.333 rather close to the “dominant” pole.

## Slide 41
Section: 3
Code
PID
I am less confident of the accuracy of the prediction, nevertheless based upon the dominant pole I predict a 2% settling time of about 4/2.0924 = 1.9117 sec and zero overshoot. The DC gain is Gcl(0) = 1 so the steady-state output for a unit step input is exactly unity and I am fully confident in this assertion.

## Slide 42
Example 3.1: Proportional Integral Controller
Section: 3
PID
The steady-sate error to a step input is indeed zero. The percentage overshoot is not zero, it is 1.26% but this is obviously small. The 2% settling time is 0.618 sec and again is actually less than predicted.

## Slide 43: Note
No-one has ever really successfully developed a serious and generally applicable procedure for the design of PID controllers. The design remains more of an art than a science. Having a sense of roughly how each gain will affect the behaviour is of course very useful, but the bottom line is that one improves ones design skills in this respect through practice only. Of course various researchers have tried to develop systematic design procedures. The most famous of these are probably Zeigler and Nichols (who produced a number of sets of “tuning rules”, i.e. systematic rules for selecting the gains kp, ki and kd) and Ästrom (who produced a rather clever algorithm, in part based upon the Zeigler and Nichols tuning rules, to get a three term controller to tune itself).
Section: 3
PID

## Slide 44: Note
Self-tuning three term controllers either based on, or at least inspired by, Ästrom’s work are now quite prevalent. These systems in principle eliminate the need for human design. Moreover, if the plant changes for any reason (e.g. aging or upgrading) the controller will automatically adapt to maintain good closed-loop performance. The disadvantage of these systems is that they tend to impose a one size fits all control regimen. The reality is that a once-off PID controller designed by a human expert for the specific plant in question will almost always give a better closed-loop performance than the more generic controller automatically designed by self-tuning. Industry has a choice of three options: (i) have a PID control design practitioner on the permanent staff, (ii) hire a PID control design master-practitioner to consult when required or (iii) make a once-off investment in self-tuning controllers.
Section: 3
PID

## Slide 45: Note
The latter choice would appear to be the obvious one from a purely economic point of view if we were discussing a situation where only one controller was required. A typical industrial plant may be expected to have, at an absolute minimum, tens of controllers and at a maximum millions. The decision is as much management as technical. Increasing importance of the energy issue, for whatever reason it arises, may be expected to tilt the choice more in favour of options (i) and (ii) than has been the case in the recent past. Even minor improvements in controller performance can accumulate to percentage improvements in efficiency. This is not enough to justify the cost of design and implementation with oil plentiful, prices below 40 dollars a barrel and few serious costs associated with emissions, but arguably is enough with growing competition for oil, prices above 100 dollars a barrel and mounting pressure for the introduction of serious costs on emissions.
PID
Section: 3

## Slide 46: Dominant Pole Placement
I deduce that the idea of dominance is useful and that a knowledge only of the location of the dominant pole or poles, minus any other knowledge of the closed-loop system permits prediction of speed of response and level of overshoot in the event of a unit step input. I accept that sometimes this knowledge is not in fact sufficient and the predictions can be wrong. Sometimes the predictions are conservative and actual performance is better. But sometimes predictions are optimistic and actual performance is worse. Accepting all of this I have a means for translating specifications concerning the desired system behaviour (namely unit step response) into desired dominant pole locations.
Section: 3
PID

## Slide 47: Dominant Pole Placement
I deduce that the idea of dominance is useful and that a knowledge only of the location of the dominant pole or poles, minus any other knowledge of the closed-loop system permits prediction of speed of response and level of overshoot in the event of a unit step input. I accept that sometimes this knowledge is not in fact sufficient and the predictions can be wrong. Sometimes the predictions are conservative and actual performance is better. But sometimes predictions are optimistic and actual performance is worse. Accepting all of this I have a means for translating specifications concerning the desired system behaviour (namely unit step response) into desired dominant pole locations.
Section: 3
PID

## Slide 48: Dominant Pole Placement
Specifically if the desired 2% settling time is Ts or better then the dominant pole/poles must have a real part more negative than -4/Ts . I deduce this from the fact that in either event (dominant pole or poles) the 2% settling time is approximately 4/s where –s equals the real part of the dominant pole or poles. If the desired overshoot is F % or less then this may be translated into a minimum acceptable damping ratio and this in turn translates into a maximum acceptable angle for a sector about the negative real axis in which the pole or poles must lie.
Section: 3
PID

## Slide 49: Dominant Pole Placement
So the what we have achieved in all that has been said to date is simply to argue that for perfect tracking of a step input there must be an open-loop pole at zero and that for suitable response to a step we require that there exist either a dominant real closed-loop pole or a dominant pair of closed-loop poles and that these poles lie sufficiently far into the left half plane (for speed) and inside a sufficiently narrow sector centred on the negative real axis (for overshoot limitation). Now we need to learn how to design controllers so that these specifications are met. The resulting control methodology may be called “dominant pole placement”.
Section: 3
PID

## Slide 50
Root Locus
Section: 3
Closed-loop TF:
Assume ideal sensor
Assume P controller
Closed-loop poles are roots of:
i.e. of:
where
PID
Notes: Dp(s)+kNp(s) is the closed-loop characteristic polynomial in this case.

## Slide 51
Root Locus
Section: 3
Definition 3.1: The positive root locus of a rational polynomial G (s) = N(s)/D(s) is a plot of the roots of the polynomial
for all non-negative k from 0 to +∞.
Example 3.2:
roots:
PID

## Slide 52: Note
I would expect a reaction to this definition of the root locus something along the lines of “so what ?”
But suppose you were designing a P controller. The closed-loop poles are now the roots of a polynomial equation of the form Dp(s)+kNp(s) where k is the proportional gain kp. Accordingly the root locus of Gp=Np/Dp will indicate what kind of affect this single design parameter can have on the closed-loop poles. If you bear in mind that we have already argued that many specifications can be translated into desired closed-loop pole locations then you might begin to get a sense that the root locus could be useful.
Section: 3
PID

## Slide 53: Note
Of course a plot is only useful if you can draw it and given its definition one would not expect to be able to draw the root locus since we cannot (apart form numerically) credibly solve for the roots of polynomials. but the example shows that the root locus can be quite simple.
In this case intuition leads us astray. We can in fact in general make a number of observations which combined permit us to draw rather credible approximations of the root locus. Moreover Matlab has a command rlocus which will draw the root locus for you. One could well be forgiven for wondering why I am then bothered with approximately drawing it myself. The reason will only become clear when we use it to design controllers.
Section: 3
PID

## Slide 54: Note
I should note, to be fair, that the root locus was introduced in the 1940s and 1950s by Evans.
Section: 3
PID

## Slide 55
Drawing Rules
Section: 3
PID
degree of D = n and degree of N = m.
Rule 1: The positive root locus has n branches
Assume
Example 3.2:
2 branches

## Slide 56
Drawing Rules
Section: 3
PID
Rule 2: Every branch starts at a pole,
i.e. at a root of D(s).
Example 4.2:
Both branches start at
s = -1
Notes: Proof: for k=0 the polynomial is D(s).

## Slide 57
Drawing Rules
Section: 3
PID
Rule 3: Every branch ends either at a zero,
i.e. at a root of N(s), or as an asymptote at angle.
Example 3.2:
There are no zeros.
Asymptote angles:

## Slide 58
Drawing Rules
Section: 3
PID
Rule 4: There are n-m asymptotes and they all
intersect on the real axis at
Example 3.2:
Notes: pi denote the poles (i.e. the roots of D(s)) and zi denote the zeros (i.e. the roots of N(s)).

## Slide 59
Drawing Rules
Section: 3
PID
Rule 5: A point s on the real axis is on the positive
root locus iff the total number of poles pi and zeros
zi to the right of the point is odd.
Example 3.2:
-2 not on +ve root locus as 2 poles and 0 zeros to right.
1 not on +ve root locus as 0 poles and 0 zeros to right.
Notes: In fact only one point on the real axis is on the positive root locus in this case, that point being s = -1.
There are other drawing rules, but they have faded in significance with the advance of power and availability of numerical tools.

## Slide 60
Example 3.3
Section: 3
PID

## Slide 61: Note
3 branches, starting at 0, -4, -8. Denoted by crosses.
1 branch ending at -2. Denoted by open circle.
2 branches end on asymptotes at specified angles intersecting at -5.
Real axis between -2 and 0 on root locus. Real axis to left of -4 on root locus. Rest of real axis not on (positive) root locus.
Finally note symmetry with respect to real axis due to fact that roots of real polynomials occur in complex conjugate pairs.
Section: 3
PID

## Slide 62
Example 3.4: PI Controller
Section: 3
PID

## Slide 63: Example 3.4
The open-loop, uncontrolled step response reveals no overshoot (there is a dominant pole at -4 so no surprise there) and a 2% settling time of 1.15 sec. This is already probably to be considered a good performance. The steady-state output however is 1/32 = 0.0313 which is dreadful. The system does not track a step input at present.
Section: 3
PID

## Slide 64: Example 3.4
Suppose the specification of performance is as follows.
The system should track a step input with zero error.
The 2% settling time should be about 2 sec or better, i.e. worse than current.
The overshoot should not exceed 5%, not much worse than current.
Section: 3
PID

## Slide 65: Example 3.4
The first specification requires that there should be a pole at s = 0 in the open-loop transfer function. As there is no such pole at present it must be introduced by the controller, i.e. the controller requires an integral term. Now I would never advocate introducing just an integrator (i.e. an I controller). I might as well illustrate why here. Essentially if I introduce an open loop pole at 0 then there will be an extra branch of the root locus starting at this pole, i.e. close to the right half plane (RHP). I will need to have a reasonably high integral gain to ensure stability.
Section: 3
PID

## Slide 66: Example 3.4
If I only introduce an integrator then the number of open-loop poles increases although the number of open-loop zeros does not. The relative degree n-m increases. In this case the relative degree of the plant is 2, so with the addition of one extra pole and no extra zero the relative degree becomes 3. The number of asymptotes equals the relative degree. Accordingly I now have 3 asymptotes and they will be at the angles 60o, 180o and 300o. The first and third go into the right half plane. Accordingly for large integral gain the system becomes unstable.
Section: 3
PID

## Slide 67: Example 3.4
Two issues arise. Firstly the system is no longer fail safe. If an electronic component in the integrator breaks the effect of this may be that the integral gain becomes very large. As a result two closed-loop poles move into the RHP and the closed-loop system is unstable. In practice some signal will be driven to its limits and this may damage or even destroy the system. Secondly the only way to avoid this instability is to have a low integral gain. But this means that we have not necessarily “travelled sufficiently far down” the new branch of the root locus which starts at the introduced pole at 0. In short the closed-loop performance is likely to be insufficiently fast if it is not unstable.
Section: 3
PID

## Slide 68: Example 3.4
Very well I need to introduce an integrator but not just an integrator. Since I treat differentiators with a general air of distrust I might decide to try for a PI controller.
Section: 3
PID

## Slide 69
Example 3.4: PI Controller
Section: 3
PID

## Slide 70
Example 3.4
Section: 3
PID
3 branches starting at: 0, -4 and -8
1 branch ending at: -z
2 asymptotes. Angles: p/2, 3p/2, sa= (z-12)/2
Real axis between -8 and -4 and between –z and 0 on positive root locus if z < 4.
For stability will require z > 0.
Sample plot (z = 2) as above.

## Slide 71: Example 3.4
My specifications on step response determine that my dominant pole or poles should have real part less than -4/2 = -2. I may determine that since the maximum overshoot acceptable is rather small I should actually aim for no overshoot, i.e. for a dominant real pole. After all I am dealing with approximate procedures applied to approximate models. I am likely not to get what I ask for so I better ask for too much, hoping that what I do get is sufficient. I see that there is some hope that I may achieve a dominant real closed-loop pole if I choose 0 < z < 4, but for this pole to be less than -2 will require 2 < z < 4, with ideally a reasonable gap between 2 and z.
Section: 3
PID

## Slide 72
Example 3.4
Section: 3
PID
Try z = 3.5.
For dominant pole close to -2, use rlocfind.

## Slide 73
>> Gp = tf([1],[1 12 32])
>> Gc = tf([1 3.5],[1 0] controller with unit gain
>> Go = series(Gp,Gc)
>> rlocus(Go) draw root locus
>> rlocfind(Go) find gain at breakpoint
Section: 3
Code
PID
rlocfind produces an interactive plot. Place crosshairs just to the left of -2 on the branch of the root locus which will contain the dominant pole. In the command window Matlab reports:
ans =
17.5548

## Slide 74
Example 3.4
Section: 3
PID
Closed-loop poles: -4.8812 +/- 2.0808j, -2.2375
Not wanting to be too fussy I try k = 18. This gives:
I have a dominant pole at -2.2375. I expect a first order response with a time constant of 1/2.2375 = 0.4469 sec or 2% settling time of about 4/2.2375 = 1.7877 sec.

## Slide 75
>> Gideal = tf([1],[1])
>> Gcl = feedback(18*Go,Gideal)
>> pole(Gcl) find closed-loop poles
>> step(Gcl) find closed-loop step response
Section: 3
Code
PID
I achieve an approximately first order response with a 2% settling time of 1.7 sec.

## Slide 76: Note
In this case the pole locations appear to rather accurately predict the closed-loop performance, the introduction of a zero at s = -3.5 notwithstanding.
It hardly needs to be observed that the solution kp = 18 and ki = 63 was far from unique. This is typical with design. The advantage is that we may bring additional requirements into the process. We may demand for example that the controller gains and their ratio should neither be too large nor too small, as otherwise there may be difficulties in fabrication and robustness. We might consider failure modes (i.e. gains failing high or low) and demand that the system be fail safe. We could consider the effects of parameter drift (with changing temperature for example) and look for reduced sensitivity.
Section: 3
PID

## Slide 77
Recall: First Order System
Section: 3
PID
Specification: | Symbol: | Approximation:
10% to 90% rise time | tr | 
Settling time | ts(2%) ts(5%) | 
Overshoot | PO% | 0%

## Slide 78
Formulae approximate even for second order systems
because they assume a special form for the numerator.
Accordingly we employ them with a very strong caveat.
Section: 3
PID
Recall: Second Order System
Notes: Formulae for time to overshoot and overshoot are exact for canonical second order system. The formulae for the settling times are reasonable approximations for the second order canonical system. The formula for rise time is hard to acquire.

## Slide 79
Example 3.5
Section: 3
PID
Require zero steady state error to step input, maximum of 5% overshoot and maximum of 1.5 second 2% settling time. As the plant already has a pole at zero, zero steady-state error will be achieved automatically when system is put into unity negative feedback loop.
Translate specifications into desired closed-loop dominant pole locations:

## Slide 80
Example 3.5
Section: 3
PID
So we require a dominant pair with a damping ratio in excess of 0.7, i.e. inside a suitable sector and a real part placing them to the left of the line Re(s) = -2.6667. There is a formula for finding the appropriate sector given the minimum acceptable damping ratio but I never bother using it. Instead I use the Matlab command sgrid.
As we have no need of an I-term let us try a P contoller.
The first formula indicates that for z ≥ 0.7 one obtains PO of less than about 4.6%.
The settling time indicates that for a 2% settling time of less than 1.5 sec will a real part of the dominant pair of -2.6667 or less.
Notes: Re(s) = - zeta*Wn
Im(s)/|Re(s)| approx sqrt(1-zeta^2)/zeta.
Alternatively can work out which sector poles lie in. This is not the best way.

## Slide 81
Example 3.5
Section: 3
PID
P controller:

## Slide 82
>> Gp = tf([1 7],poly([0 -5 -15 -20]) note use of poly
>> Gc = tf([1],[1])
>> Go = series(Gp,Gc)
>> rlocus(Go) draw root locus
>> sgrid
Section: 3
Code
PID
sgrid draws the sectors which correspond to damping ratios of 0.1, 0.2, 0.3, 0.4, 0.5, 0.6, 0.7, 0.8 and 0.9. It also draws circles which are related to the natural frequency but I will not be using these. There is a variation of sgrid which accepts input arguments and supposedly draws the sector corresponding to user-specified damping ratios only. I have always found this variation to be useless.

## Slide 83
Section: 3
Code
PID
We may use the zoom tool.

## Slide 84
Example 3.5
Section: 3
PID
Use rlocfind.

## Slide 85
Example 3.5
Section: 3
PID
>> [k,poles] = rlocfind(Go) place dominant poles
k =
326.2339
poles =
-21.9025
-12.4588
-2.8193 + 0.6481i
-2.8193 - 0.6481i

## Slide 86
Example 3.5
Section: 3
PID

## Slide 87: Note
You are only finished when you have checked that the design actually meets the original specifications. Remember, there are a lot of approximations and assumptions. Be prepared for some nasty shocks when you check the actual closed loop performance. In this case clearly there is no overshoot. There is zero steady-state error of course. The 2% settling time is 1.93 sec. Accordingly we fail to meet the specification. The closed-loop poles are -21.8755, -12.4975 and -2.8135 +/- 0.5269j. The dominant pair have non-zero imaginary part which would suggest a small overshoot. As required their real part is less than -2.6667, nonetheless they fail to give fast enough response.
Section: 3
PID

## Slide 88: Note
In this case overshoot does not appear to present a problem. The complex branches of the root locus initially bends further into the LHP. Select higher up on branch.
Section: 3
PID
k =
522.3271
poles =
-22.6658
-11.3540
-2.9901 + 2.2950i
-2.9901 - 2.2950i

## Slide 89: Example 3.6 (2010 Examination)
1. A SISO, LTI plant has transfer function:
.
Find the poles and zeros of the plant. 5
Determine the step response of the plant and characterise it by evaluating the DC gain, the steady-state error, the 2% settling time and the percentage overshoot. 10
Design a PID controller such that the closed loop step response meets the following specifications:
(i) Zero steady-state error
(ii) Percentage overshoot not exceeding 5%
(iii) 2% settling time not exceeding 3 sec. 60
Confirm that specifications are met by finding the closed-loop step response and
computing relevant data. 25
Section: 3
PID

## Slide 90
>> Gp = tf([20 50],[1 4.35 21.4 7]) note use of poly
>> pole(Gp)
>> zero(Gp)
>> step(Gp)
Section: 3
Code
PID
poles: -2 +/- 4j, -0.35
zeros: -2.5
DC Gain: 50/7 = 7.1429
Steady-state error = 614%
2% settling time: 10.9 sec
PO = 0%

## Slide 91: Note
The steady-state error is very large, because the open-loop DC gain is much higher than unity.
The plant has a dominant real pole at -0.35. This predicts a 2% settling time of 4/0.35 = 11.42 sec. Although the actual value is somewhat less than this, the rough figure is correct, the settling time is rather long.
The early phase of the step response clearly indicates the presence of higher order dynamics.
Section: 3
PID

## Slide 92: Example 3.6
Zero steady state error to step: require open loop pole at 0.
2% settling time less than 3 sec: require closed loop poles to left of line Re(s) = -4/3 = -1.33.
PO less than 5%: A dominant pair with a damping ratio ξ better than 0.7 will give PO less than 4.6%
Section: 3
PID

## Slide 93: Example 3.6
I may initially attempt to meet the specification with a PI controller, since the steady-state error specification does require an I-term. As usually such a controller has a transfer function:
Section: 3
PID
I must introduce a zero as well as a pole (at 0). Before I can even draw the root locus I must decide where that zero should be. It is for this task that I find the root locus drawing rules to be useful.

## Slide 94: Example 3.6
z < 0
Section: 3
PID
There are reasons why we would never introduce a RHP zero. In this case one branch of the roots locus will pass in to the RHP and the closed loop system will be unstable. So z < 0 is a bad choice.

## Slide 95: Example 4.6
z = 0 would cancel the desired pole at zero.
0 < z < 0.35
Section: 3
PID
There will be a closed-loop pole on the branch of the root locus lying between the pole at 0 and the introduced zero. This pole will be to the right of the line Re(s) = -0.35 and is therefore not fast enough.

## Slide 96: Example 4.6
0.35 < z < 2.5
Section: 3
PID
Two complex conjugate root locus branches bend back into RHP. Does not look like we will be able to ensure all poles to left of Re(s) = -1.33.

## Slide 97: Example 3.6
2.5 < z
Section: 3
PID
Not fail safe and surely not fast enough.

## Slide 98: Example 3.6
With a PI controller there are four poles and two zeros giving 2 asymptotes. For large gain the closed-loop poles on these asymptotes are very lightly damped and give rise to a highly oscillatory component of the step response. If z exceeds 1.85 these poles are actually unstable and therefore the closed-loop system is potentially unstable. Even if z is less than 1.85 the highly oscillatory response for high gain implies very high overshoot and the closed-loop must be considered to be potentially practically unstable.
I conclude that a PI controller does not appear to offer a good solution in this case.
Section: 3
PID

## Slide 99: Example 3.6
The previous problem with asymptotes is now eliminated. With a PID controller there are four poles and three zeros giving just one asymptote which will be at an angle of 180o.
As a rule of thumb try to design controllers so that the root locus has no more than one asymptote, i.e. that the number of closed-loop zeros is not more than one less than the number of closed-loop poles.
Section: 3
PID

## Slide 100: Example 3.6
2.5 < z1 < z2
Rule of thumb: Introducing zeros reasonably far into the LHP drags the entire root locus further into the LHP and thereby improves the speed of response.
Section: 3
PID

## Slide 101: Example 3.6
2.5 < z1 < z2
As the introduced zeros are to the left of -2.5 and as this in turn is to the left of -1.33 we should be able to ensure that closed-loop poles are in the required region. Note that the damping ratio values are non-uniform.
Section: 3
PID

## Slide 102: Example 3.6
2.5 < z1 < z2
Two applications of rlocfind reveal that the higher gain is required to ensure injection of the faster poles into the required sector. With essentially arbitrary choices of z1 = 3 and z2 = 3.5 we find k = 0.75 which gives dominant pair having acceptable real part -1.79.
Section: 3
PID

## Slide 103: Example 3.6
Section: 3
PID
Closed-loop poles: -7.8816.19 +/- 5.799j, -1.7934 +/- 0.9466j.
We fail to meet the specification with an overshoot of 7.82% and a 2% settling time of 0.36 sec. The 10% to 90% rise time is about 0.096 sec.

## Slide 104: Example 3.6
In general if the overshoot is a little too high then a slight increase in the derivative gain may affect a suitable improvement. Try
Section: 3
PID
We meet the specification with an overshoot of 2.11% and a 2% settling time of 1.71 sec. The 10% to 90% rise time is about 0.067 sec.

## Slide 105: Example 3.6
Given the chosen controller the resulting closed-loop poles are: -27.9083, -3.6143, -1.4137 ± 1.3802j.
We have a dominant pair: -1.4137 ± 1.3802j. The poly command reveals that these are the roots of s2+2.8274s+3.9036. Equating to
Gives that the dominant pair have a damping ratio ξ = 0.7155 and a natural frequency ωn = 1.9758 rad/sec. From the approximate formulae I therefore expect:
PO = 4% , ts(2%) = 2.83 sec , tr = 0.911sec.
But get: PO = 2.1% , ts(2%) = 1.71 sec , tr = 0.067 sec.
Section: 3
PID

## Slide 106: Example 3.6
The example is revealing the fact that the locations of the closed-loop poles and the dominance properties of those poles is indicative of closed-loop performance only. In this case the closed-loop performance is better than that predicted by pole location only. The reason, in particular for the rise time, is that there are much faster poles present which play a significant role in the early phase.
Section: 3
PID

## Slide 107: Example 3.6
The plant has poles at -2 ± 4j and at -0.35.
It is the latter, dominant, pole which has the greatest influence in this case upon the rise time which we found to be a rather sluggish 6.15 sec. It should be noted however that the plant does have poles at -2 ± 4j and accordingly it is physically reasonable for it to be able to react to step inputs with the speed of a system having poles at -2 ± 4j.
These poles have damping ratio 0.4472 and natural frequency 4.4721 rad/sec. From the approximate formula I would expect a rise time of about 0.4025 sec. I find it implausible that I could reduce this rise time by about 80%.
Section: 3
PID

## Slide 108: Example 3.6
The discrepancy suggests that, at least in the early phase, the actual closed-loop system will not react as fast as the approximate model predicts. I would not be overly concerned about this. The model is predicting an early phase response speed far in excess of what is required. If the actual response fails to be as fast it does not matter since I never required it to be this fast in the first place. As long as the middle and late phase response of the actual system is rather similar to that of the model everything will be okay. The best way to check that this is indeed the case is to build the closed-loop system. Usually any problems found can be resolved with a little tinkering.
Section: 3
PID

## Slide 109
Section: 3
The step response of a closed loop system is determined in large part by the location in the complex plane of the dominant closed-loop poles.
The root locus is a tool which can be employed in the design of controllers. The objective of the design is to ensure acceptable step response via the placement of the dominant pole(s).
Section 3 - Conclusion
PID